## Slide 1
Customer: C-H Payment To: Southern Power
Billing Period From: 9/1/95 12:00:01 AM To: 9/30/95 12 Midnight
Notes: 1
29
31
1

## Slide 2: Energy Billing Concepts
Energy Usage (KWH)
Peak Demand Charge (KW)
  Demand=average load over a pre-set interval (15-, 30-, or 60-minute).
Rate Schedules
  Seasonal, Weekday/Weekend/Holidays, Time Period
  On Peak/Multiple Off Peak
  Ranged Charge - the more the less per unit
Other Charges
  Service Charges, Taxes, Credits, Power Factor, etc.
Notes: 2
30
29

## Slide 3: Coincident Peak Demand
Utility Meter
Tenant #1
Tenant #2
Coincident Peak
Demand determined
at Utility common
coupling point.
Tenant demand
charge occurs at
the highest
demand of the
entire building.
Notes: 3
31
30
1

## Slide 4: Traditional Implementation
Traditional Allocation
  Square Footage
  Equal Share
  Guess Work
Transmission
4,500 sq ft
Heat
Treat
450 sq ft
Office
Drawbacks
  Unfair
  Time Consuming
  No Incentives to Conserve Energy
Notes: 4
32

## Slide 5: Traditional Implementation Glass Meters
Wall Mounted Meters Stacks
33.6 Square Feet
49 Hour installation time
Utility Meters bought & installed separately
Main
Pull
Box
20”
20”
19”
19”
43”
High
50”
High
55.5”
High
55.5”
High
Notes: 5
33
32
1

## Slide 6: Traditional Communication Implementation
Watt Xdcr
BKR
BKR
Watt Xdcr
Analog Inputs
PLC
Notes: 6
34
33
1

## Slide 7
INCOMING
SUBSTATION
LV
SUBST.
MV
SWGR
LV
MCC
ADJUSTABLE
FREQUENCY
DRIVES
MV MCC
ENCLOSED
CONTROL
PANELBOARD
ATS
LIGHTING
Panels
Notes: 7
35
19
19
That information is available throughout the distribution system and can be tied together and displayed on a personal computer in the maintenance office, engineers office, or anywhere else it is needed.

## Slide 8: Incoming Meter: IQ Analyzer
+/-0.2% Measured, 0.4% Power
ANSI Revenue metering accuracy
Whrs, Varhrs, Vahrs, Demand current, watts, vars, va
Digital/Analog I/O
Self Powered or separate control power
No PT’s through 600 V
Best choice for Utility common coupling point.
Notes: 8
36
39
11

## Slide 9: Feeder Meter: IQ DP 4000
RMS sensing
+/-0.5% Measured, 1.0% Power
Whrs, Varhrs, Vahrs, Demand current, watts, vars, va
Time/date stamp min/max
Power quality information
Self Powered or separate control power
No PT’s through 600 V
Notes: 9
37
40
12

## Slide 10: Submeter:Energy Sentinel
Watts, Peak Demand, kW-hours
1% Accuracy including CT & PT
Breaker Mounted
  15-400 Amp, 120-600 VAC
  No CT’s/PT’s
Universal, Internal CT’s
  To 400 A, any disconnect
Universal, separate CT’s
  To 4000 A, any LV circuit
Lowest installed cost, high accuracy submeter
Notes: 10
38
41
14
Or a meter that monitors energy by plugging onto a molded case circuit breaker..
The protective relays are also used for metering..

## Slide 11: Feeder Meter: IQ Data Plus II
+/- 1% Measured, 2% Power
Demand watts: Selectable fixed window or sync pulse, resettable
kWhrs: Cumulative, resettable, selectable pulse output
Alarm/Trip Outputs
Self Powered or separate control power
No PT’s through 600 V
1 Style Number
Notes: 11
39
42
13
Such as the IQ Data Plus II, a multifunction meter....

## Slide 12: Energy Trip Units: Digitrip 910/810/800
RMS Sensing (Main function Protection)
Energy Parameters
  Current, Individual phase & Ground
  Instantaneous & Demand Watts
  W-Hrs
  Power Factor
  Operational Data
Accuracy 2% amps, 5% energy
Notes: 12
40
43
16
Similar functions provided in the LV swgr...

## Slide 13: MCCB Meter: Digitrip OPTIM
RMS sensing
70-5000 Amp trip units
Primary Function Protection
Energy Monitoring
  Amps
  watts
  demand, kWH
  PF, VARs
  Harmonic information (%THD)
  Operational data
Accuracy 2% amps, 5% energy
Notes: 13
41
44
17

## Slide 14: IMPACC: AI Module
Cutler-Hammer
Analog Input
Module
Thirty two 0-20ma, 4-20ma transducer inputs.
24VDC power supply to develop ma input from dry contacts up to 2000 feet away.
On board trending, BTU calculation, run time calculation
Supports scaling in Module
Allows complete energy monitoring beyond traditional electrical paramaters
  Oil, Gas, Compressed Air, Water, Sewer
Notes: 14
42
45
23
This unit, combined with the IQ 1000 II is the only package that automatically adjusts the trip curve to adjust for both a hotter AND cooler running motor... and it can be mounted in the motor conduit box, greatly reducing installation and wiring costs (3 wires from the motor vs 30...).
(REVIEW INFORMATION ON THE SLIDE)

## Slide 15
IQ Drive Controller
IQ DP 4000
Digitrip Optim
Energy Sentinel
DP4000
Digitrip 810
INCOMING
SUBSTATION
LV
SUBST.
MV
SWGR
LV
MCC
ADJUSTABLE
FREQUENCY
DRIVES
MV MCC
ENCLOSED
CONTROL
DP4000
IQ DP4000
Energy Sentinel
IQ Analyzer
DP4000
PANELBOARD
IQ DP4000
Digitrip Optim
Energy Sentinel
ATS
IQ Transfer
LIGHTING
PANEL
Pow-R-Command
Notes: 15
43
19
19
That information is available throughout the distribution system and can be tied together and displayed on a personal computer in the maintenance office, engineers office, or anywhere else it is needed.

## Slide 16: Power Distribution - Reacting
Notes: 16
44
This reflects a “manual” attempt at power monitoring. It requires a person walking the plant, clipboard in hand, manually taking data, then filing it. When data is needed, routing through all the data is virtually impossible. In addition, chances that he/she were at the right place when a peak occurred, or caught the excessive runtime the first couple of times around are very unlikely. In addition, since they are “making the rounds”, they don’t have time to do the preventative maintenance...

## Slide 17: Energy Monitoring Applications
Local/
Remote
Display
Central
Billing,
Trending
Trending,
Alarming,Control
Graphics,
Special Displays
IQ CED,
BIM
E-Bill
Series III w/
Enhanced
Graphics
$
Notes: 17

## Slide 18: IMPACC: Remote Monitoring
BIM, AEM II,CED
Local or Remote monitoring for multiple devices.
Up to 8500 feet from devices
Lowest cost central energy monitoring solution
Replaces monthly walk around meter readings
Notes: 18
46
46
26
...and it can be displayed at a single point on the gear, or mounted remotely from the gear in a reasily accessable area (maintenance office, for example)

## Slide 19: Traditional Implementation
Wall Mounted Meters Stacks
33.6 Square Feet
49 Hour installation time
Utility Meters bought & installed separately
Main
Pull
Box
20”
20”
19”
19”
43”
High
50”
High
55.5”
High
55.5”
High
73.5”
High
36”
Pow-R-Line C
vs
Meter Stacks
Wall Mounted
18.375 Square Feet
16 Hours
46% wall space savings
Notes: 19
47
35
1

## Slide 20: Traditional Implementation
Watt Xdcr
BKR
BKR
Watt Xdcr
BKR
BKR
Modbus Gateway
or MINT II
E
S
E
S
Analog Inputs
Serial Input
PLC
Savings
  No CTs
  Eliminates 10 wires/ckt
  No Analog cards
  Installation time
  Savings $391 per ckt.
Notes: 20
48
36
1

## Slide 21: Traditional Implementation
30K-50K
Savings
In Addition
there is an
installation
savings.
Number of Devices
0
10
20
30
40
50
60
70
80
K$
IQ Energy Sentinels
with MINT II
Transducers with CTs
PLC Analog Input Cards
10
60
50
40
30
20
Notes: 21
49
37
1