## Slide 2
IMPACC New Products
ICONI
  1/2 size; multiple CONI; thruput enhance
  Auxilary Input Contact
  Resistor
Analog Input
  32 Inputs; Pulse counter; scalable
  Instant., avg., cumulative, time stamp
  4-20 mA, 0-10V; time on/off; 120V
  PONI
  Approx $1900 net user; 8/96
L-PONI

## Slide 3
INCOM Wiring Rules: Topology
Bus -or Single star
Maximum of long lines from star: 5
Line termination:
  none for tap
  100 ohms at end of long line
Maximum cable length between ends of longest lines: 10,000 feet

## Slide 4
INCOM Wiring Rules:Attenuation
Total system capacity: 25 dB
Attenuation per device: 0.01 dB
Attenuation for approved wire types:
  Cable type Attenuation/1000 feet
  IMPCABLE 1.6 dB
  Beldon 9463 family 2.0 dB
Number of long lines Attenuation
3 4 dB
4 6 dB
5 8 dB

## Slide 5
INCOM Wiring Rules:Definitions
Daisy chain
  point to point wiring between devices or clusters of devices
Star
  Single point with a number of long lines emanating from it
Long line: >200 foot wire run
Simple Tap: <200 foot connection to cluster of devices

## Slide 6
3,000 ft, 150 devices
A
1,500 ft, 200 devices
1,500 ft, 100 devices
5,000 ft, 100 devices
B
C
D
INCOM Wiring Example

## Slide 7
INCOM Wiring Example Solution
TOPOLOGY: Single star with four long lines
PROCEDURE:
  Compute “allowed attenuation” for star system
  Total system capacity 25 dB
  Deduct for star - 6 db
  Net capacity 19 dB
Calculate attenuation of each long line:
  Line Length Devices Attenuation
  A 3,000 150 (2dB*3)+1.5=7.5 dB
  B 1,500 200 (2dB*1.5)+2=5.0 dB
  C 1,500 100 (2dB*1.5)+1=4.0 dB
  D 5,000 100 (2dB*5)+1 =11.0 dB

## Slide 8
INCOM Wiring Example
Add two largest attenuations:
  A+D=18.5 db
Compare to allowed attentuation:
  18.5 dB<19 dB, therefore the network is OK